My keypad display is blank, OC, flashing between numbers

My Keypad displays OC, is blank, or flashing between 2 numbers (00-31 or 17-00) These symptoms indicate that the keypad is not receiving data from control panel. This FAQ will explain how to address a keypad and enable it in programming. Topics:  Set or Read the keypad address  Select the correct address for the keypad  Verify that the address is enabled in programming.  Verify the wiring  Isolate the keypad Set or Read the keypad address  The keypad address is set by holding the 1 and 3 keys together immediately after powering up the keypad. The display will show you the existing address. You may now key in the correct address. Press * to save it.  The 6128RF and 6150RF have an internal program mode used to set their address. Refer to their installation instructions for more information. Select the correct address for the keypad  Depending on the control panel that you have, you will need to select an address in the following range: Vista-10/15/20/30 (including se) Non addressable – set all keypads to address 31 Vista-10P/15P/20P Set the first keypad to address 16, others may be 17-23 Each device must have a unique address Vista-40 Set the first keypad to address 00, others may be 01-15) Each device must have a unique address Vista-50, 100, 128, 250 and 32 Set the first keypad to address 00, others may be 01-30) Each device must have a unique address  If the system uses addressable keypads, each address must be enabled in the panel programming. The first keypad on these is always enabled and cannot be changed. Verify that the address is enabled in programming. Depending on the control panel that you have, you will enable the keypads differently: Vista-10/15/20/30 (including se) Nothing required in programming. Vista-10P/15P/20P Enable keypads 17-23 in program location *190-*196 for more information. Vista-40-Vista250 and 32FB Enable additional keypads in device programming. Verify the wiring  Make sure that the keypads are connected to the proper terminals on the control panel.  Check voltage on the keypad data wires with reference to BLACK (negative):  RED should be 13.6VDC  YELLOW should be fluctuating11-13VDC  GREEN should be close to 0VDC (a few millivolts with some fluctuation)  The GREEN wire is most likely the problem based on the symptom described. Isolate the keypad Try connecting the keypad directly to the panel with all other keypad data wires removed and retest.