I am getting a check on a hardwired zone, why?

FAQ 14007466

The following will explain why a hardwire zone may go into check. Topics:  - Zone types that cause check  - High resistance sensing  - Double balanced zone configuration  - Hardwire Zone Short-detection - Zone types that cause check Zone types 05 (trouble) and 09(fire) can cause a CHECK if the zone is faulted. If this is the case, strap the zone with a resistor and see if it clears. It is likely a field wiring issue. Configurable zone types (90/91) on the Vista-15P and 20P may go into trouble based on their programming. - High resistance sensing The Vista-15, and 20se series controls can sense if a zone has a higher resistance than it should. The panel zone should be 2000 Ohms (+/- 300 Ohms). If the loop resistance rises above 2300 Ohms, a trouble condition is annunciated. A bad splice in the field wiring often causes this condition. If this is the case, strap the zone with a resistor and see if it clears. It is likely a field wiring issue. - Double balanced zone configuration Documented as a feature of the Vista-20P, This feature basically creates a high resistance trouble if a tamper switch is violated. - Hardwire Zone Short-detection This feature is an option only on the Vista-15 (not the 15P or any version of the 20) If *30 = 1, a short on a hardwire burg zone is treated as a trouble condition.